NXL SETTINGS AND WIRINGS FOR 
ALLWAYS USE STD MODE

	Code
	Parameter
	Default
	Setting
	Note

	P6.3.1
	Parameter set
	0 (no action)
	5 (load factory default)
	

	P6.10.2
	Fieldbus protocol
	1
	1 (Modbus)
	

	P6.10.3
	Slave address
	1
	as required by application
	

	P6.10.4
	Baudrate
	5 (9600)
	6 (19200)
	

	P6.10.5
	Stop bits
	0 (1 stopbit)
	1 (2 stopbits)
	

	P6.10.6
	Parità type
	0 (parity none)
	0 (parity none)
	


	P6.10.7
	“VFD Offline” Activation alarm delay
	0 sec
	20 sec
	

	Code
	Parameter
	Default
	Setting
	Note

	P3.1
	Selection of control place 
	2 (keypad)
	3 (fieldbus)
	When P3.1 is set to “1” the start-stop of the inverter is from the DI1 of the inverter and not from the MODBUS communication. N.B. If this parameter is set to 1, the VFD will disable the “Field bus Offline allarm”

	P2.2.21
	Fieldbus frequency reference selection
	3 (FB Speed Reference)
	3 (FB Speed Reference)
	

	P2.1.14
	I/O reference
	
	3 Modbus
	


Wiring connection between the NXL Inverter and the PCO controller’s PCO100FD10 (modbus field card)
A ( -
B ( +

11 ( Gnd
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Inverter Setup for Fixed speed with Autorester on power supply provided by the E.P.
Wiring: link out terminals 6-8

Configuration: STD

P3.1 = 1 (I/O Terminal)

P3.2 – Setpoint in Hz

P2.1.14 = 2 Keypad reference
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